EnergyPro 7 Tutorial: From Scratch

Student Store

Open EnergyPro

File

New

Undefined

Rename to “STUDENT STORE”

Front orientation: South (it might say 180 deg)

Location: Corona, CA

RC on STUDENT STORE

Add Plant (this is your domestic hot water)

Name it DHW

Give it Standard Gas 50 gal or less

RC on DHW

Add System (this is the HVAC unit)

Rename to HVAC

RC on HVAC

Add Zone

Name it Zone 1

Note: we will need 5 Zones. Make them.

Zone 1 will hold the Store

Occupancy: Retail sales: Wholesale

Zone Type: Conditioned

In Zone 1, pick the  “Mechanical” tab. There is a checkbox for us…..Demand Control Ventilation.

The Zone will have a ceiling height of 9’0” (use average of rooms in the zone if there are multiple rooms). Same with the window head heights. Floor to Floor is 12’0”

RC on Zone 1 ….Add Room

Name the room: STORE

Area: 53*35= 1855

RC on STORE

Add Ext Wall

Name it “SOUTH WALL”

Area: 53*16=848

Orientation: South

New Assembly: R-19 Wall (we’ll give the wall smarts later)

RC on STORE

Add Ext Wall

Name it: EAST STORE WALL

Area: 35*16=560

Orientation: East (may say 90…North is zero……get it?)

Back to SOUTH WALL

RC…Add Window

Note: We have 5 windows, but only 2 sizes….so we will create TWO windows on the south wall to start

On first window, name it “Window A”

Area: 24

Pick second window, name it “Window B”

Area: 12

Select window A….RC….Copy

SOUTH WALL….RC Paste

Select window B…..RC…..Copy

SOUTH WALL….RC…..Paste twice

Note: you can drag them in order

South wall….RC…Add Door

Name it STORE DOOR

Area: 48

We’ll make it smart later

Select STORE

RC…..Add….Slab on Grade

Name it Store Slab-on-Grade

Area: 53*35=1855

Ext Per: 35+53+35=123’

Select STORE

RC….add Roof

Name it Store Roof

Area: 1855

Choose R19 Metal Deck Roof

(no orientation since it’s flat)

RC on STORE

Add Ext Wall

Name it: WEST STORE WALL

Area: ??	Orientation: ??

Select STORE

RC….Add Lighting

Note: all the lights are the same

Name the light CFL

Use the  2 Lamp 54W Linear T5 HO ElectD 125W Flourescent (24th on list)

Multiplier: 9

Note 125W*9= 1125W….so you do NOT need 9 lights in the tree!

Control: Demand Responsive

Zone 2 will be BOH, MEN’S, WOMEN’S

Zone 2

Occupancy: Bathroom

Ltg 90.1: Restrooms

Check Demand Control Vent (under Mechanical)

RC…add Room

MEN’S

RC…add Room

WOMEN’S

RC…add Room

BOH (Back of House)

Like Zone 1, Zone 2 will have a ceiling height of 9’0” (use average of rooms in the zone if there are multiple rooms). Same with the window head heights. Floor to Floor is 12’0”

MEN’S

Area: 8*19=152

RC on MEN’S

Add…Ext Wall

Note: For now…..EnergyPro ONLY NEEDS EXT WALLS!!!

Name it NORTH MENS WALL

Area: 8*16= 128

Orientation: North

No door needed…it’s inside

RC on MEN’S

Add Lighting

Name it BA LIGHT

Mult: 2

Luminaire: 54W T5 (21stth on list) (Note 62W performance)

Control: Demand Responsive

RC on MEN’S

Add Roof

Area: 152

R-19 Flat Metal Deck

Name it “Bath Roof”

Notice MEN’S and WOMEN’S are the same???

Delete WOMEN’S

Pick MEN’S…RC….Copy

Pick ZONE 2…Paste

Rename the second Men’s room “WOMEN’S. Faster!! (don’t worry about the names, just organizational)

Note: Copy/Paste in EnergyPro is important to creating an energy model in a reasonable amount of time!

Zone 3 will be STORAGE

Zone 4 will be Office

Zone 5 will be Conf and Staff Lounge

Zone 3

Zone Type: Unconditioned

Occupancy: Comp Bldg Com & Ind Storage

Storage

Note Storage Zone is Unconditioned. YES…you still need to create it. Lighting. Adjacent rooms and adjacent to outside.

Area: 15*31=465

Storage Lights

Choose the 4lamp 4 ft T8 Energy Saving ElecRO (60 on list) at 91 W

Mult: 3

Control: Demand Responsive

Add Slab on Grade

Name it Storage Slab-on-Grade

Area: 15*31=465

Ext Per: 15’

Storage

Add Roof

Name it Storage Roof

Area: 465

R-19 Metal Deck

Show calculations on Lights: Zone Lighting T-24	W/sq.ft to get close. So .6 times 465 =  279. If you aren’t close to the T-24 calc, you may have too much (or not enough) light for the space. We are 273….nice!

That should give you enough to finish the EnergyPro model. Ext walls, doors, windows, slabs, roofs, and lights….

Save as: STUDENT STORE 7.bld

Calculate Loads

Show warnings and fix (yes…I made a few on purpose )

Check the building tree to insure all walls, slabs, roofs, lights, windows and doors are in….and accurate properties assigned. Compare with Mr. Brown’s model…..did you forget anything???

Our Sensible Load is about 144,000 BTU’s…let’s find a system that is close:

HVAC

New System

Import Air Conditioner

Show Output Filter

I put 130000 to 160000

Type: Single Package:

I picked the Carrier 48HCEE14A2M5032329 (more on those long numbers later)

It has an output of 146,000 BTU. Not bad!

Select…OK

Fans

Set the Design airflow to 4000 CFM’s (was at 0)

Input as watts: 11,900 (from spec sheet page 9)

Check Title 24 Non-Residential Performance to see if the building is meeting California’s Energy Code!

Fix the errors!

I loaded the spec sheet in the X:/EnergyPro7 Tutorial Folder

Run the NR T-24

You should see “Wrapper” dialog box and it should be “Perfoming Analysis”

Wrapper not working on mine…

Note: Didn’t like my R-19 roof. Changed to R-30. Worked.

Note: In Zone 1, Mechanical, Changed Cooling Supply Air Flowrate from 2159 to 2500. Worked.

Still more to do. Cooling is high. Lighting is great. Fans are really high. We have walls, glass, roof, etc still to manipulate.

EnergyPro Interior Surfaces

So I lied earlier about Interior walls not needing to be modeled. There are some that do need to be modeled. You MUST model Interior Surfaces between zones.

Inputting Interior Surfaces between rooms that are in same zone is not necessary. EnergyPro will not look at them.

Set the Interior surface adjacent to other room. DEMO.

If you have more than one zone, it MUST have an interior surface adjacent to the other zone(s). It can be a wall, ceiling, or floor.

You need 6 surfaces in every zone.

Every zone must have a valid floor.

On multi-story buildings:

Zones on Floor 1 would have walls, floors, ceiling (maybe no roof….)

Zones on top floor would have walls, floors, roof/ceiling

http://www.energysoft.com/faqs/

Note that you do not need to model all interior surfaces, you just need at least one between the zones. You also do not need to model the surface twice (once on each side). Inputting it once will satisfy this requirement for both the zone it is in, as well as the zone it is adjacent to.

Let’s do one:

There is a wall between the Store and the Storage room. It is 31’0” long, and 9’0”

Store….RC….add Interior Surface

Name is Storage South Interior Surface

Area is 31*9=279 sq ft

Assembly: R-15 Wall

Adjacent to: see button??

Zone 3: Storage

Now the Storage Room has the same

Now finish adding the Interior Surfaces!

Use “Reports” to get the load of the building for sizing HVAC.

File

Print Preview